[image: image2.png]HD 629.1 $3:2019 (E)

Table 10 — Indoor terminations for extruded insulation cables
(including shrouded terminations)
(see Figures 1 and 2)

Test Test sequence Test requirements
clause of (a)
EN 61442:

2005 A2 | A3

AC voltage withstand dry 5 min at 4,5 U, no breakdown nor flashover

Partial discharge at max 10pC at2 U
ambient temperature

Impulse voltage at 10 impulses of each polarity, no breakdown
elevated temperature nor flashover

Heating cycle voltage in 126 cycles at 2,5 U, no breakdown nor
air flashover

Partial discharge at max 10pC at2 Uy
elevated and ambient
temperature

Thermal short circuit 2 short circuits at L, no breakdown
(screen) ®

Thermal short circuit 2 short circuits to raise conductor to 6, of
(conductor) the cable, no breakdown

Dynamic short circuit©) 1 short circuit at 7, ©), no breakdown

Impulse voltage at 10 impulses of each polarity, no breakdown
ambient temperature nor flashover

AC voltage withstand dry 5 min at 4,5 Us, no breakdown nor
flashover

Partial discharge at max 10pC at2 Uy
ambient temperature

Humidity © 300 h duration at 1,25 Uy

Visual examination Shall be documented in the report
according to Annex C

In orderto reduce the number of test loops, test sequence A1 can be combined with test sequence A2 (perform test 1105
thentest 6to 11 and test 13). For single core range taking terminations extra test samples of the maximum size willbe:
required in orderto create 3 loops for test sequence A2
This test is only required for accessories that are equipped with a connection to, or adaptor for, the
metallic screen of the cable.
This test can be combined with the thermal short circuit on the conductor.
Applies to 3-core cables only. For the value of the current I, see 7.2.
Due consideration shall be given to ensure that the installation arrangement is representative for the
application
Not required for terminations with porcelain insulators.
No breakdown nor flashover, no more than 3 trips, no substantial damage. It is considered that a
substantial damage has occurred when it is evident that the performance of the accessory has been
severely reduced by
Toss of dielectric quality due to tracking;
andior (i) erosion to a depth of 2 mm or 50 %, whichever is the smaller, of the wall thickness of
the insulating material as applied:
andor (i) splitting of the material:
andor (iv)  puncture of the material.

NOTE Refer 1o Clause 8 of EN 61442.2005 for details of the callbralion of conductor heating current required 1o have
been carried out before the commencement of these tests.





[image: image1.jpg]tukasiewicz
Instytut Tele-
i Radiotechniczny




Warszawa, dn. 11.10.2024r.
Sieć Badawcza Łukasiewicz -
Instytut Tele- i Radiotechniczny













ul. Ratuszowa 11
03-450 Warszawa
tel.: + 48 22 619 25 12
www.itr.lukasiewicz.gov.pl
ZAPYTANIE OFERTOWE nr 080/EZ/2024
( dot.: wykonania badań wyrobu i układu pomiarowego zg. z normą HD629.1S3:2019)
Zwracamy się z prośbą o przedstawienie oferty na wykonanie badań wyrobu oraz
wykonanie układu pomiarowego zgodnie z normą HD 629.1.S3:2019
1. Sensory napięciowe typ UR66 do głowic konektorowych typu 480TB
2. Badania muszą być prowadzone zgodnie z planem badań opisanym w tabeli 10 normy HD 629.1.S3:2019

3. Badania muszą być prowadzone dla napięcia znamionowego sieci 36kV

4. Zakres badań stanowi wyciąg z normy tj. załącznik nr 1 do ww zapytania ofertowego.

           Producent: NEXANS
KOD CPV: 71355200-3 Wykonywanie badań
I. Termin realizacji zamówienia: do 8 tygodni od złożenia zamówienia

II. Termin składania ofert: do 21.10.2024r. godz. 1200.

III.  Sposób i miejsce składania ofert 
Oferta powinna być przesłana  pocztą elektroniczną na adres: adrianna.sinska@itr.lukasiewicz.gov.pl  
IV. Kryterium oceny ofert: 
Jedynym kryterium wyboru najkorzystniejszej oferty jest najniższa cena.

Cena oferty; waga kryterium – 100%

   V. Sieć Badawcza Łukasiewicz-Instytut Tele – i Radiotechniczny zastrzega sobie prawo do rezygnacji z części pozycji lub ilości
-zapytanie będzie oceniane w całości
VI. Zapytanie ofertowe zamieszczono na stronie:             https://www.itr.lukasiewicz.gov.pl/zapytania-ofertowe 
VII. Do niniejszego zapytania ofertowego nie stosuje się przepisów ustawy
z dn. 29 01.2004r. Prawo Zamówień Publicznych (Dz. U. z 2015r. poz. 2164 z późn. zm.). 
VIII. Opis sposobu przygotowania oferty
Oferta powinna zawierać co najmniej:
- nazwę i adres oferenta, NIP
- wartość oferty (netto)

- oświadczenie o braku podstaw do wykluczenia

- oświadczenie o braku powiązań kapitałowych i osobowych z zamawiającym
- ceny jednostkowe
- ilość oferowana
- termin dostawy
- pełne oznaczenie oferowanego elementu, rodzaj opakowania
Wskazane są dodatkowe informacje, np. warunki gwarancji, dodatkowe funkcje dostawy, warunki płatności i dostawy, możliwe do uzyskania upusty, maksymalny czas realizacji, kosztorys ofertowy itd.
IX. Warunki udziału w postępowaniu:
Wykonawca złoży wraz z ofertą:

1.  Oświadczenie o niepodleganiu wykluczeniu oraz spełnianiu warunków udziału w postępowaniu
2.  Oświadczenie z art. 7 ust. 1 ustawy z dnia 13 kwietnia 2022r. (Dz.U. z 2022 poz. 835)
X. Dodatkowych informacji udziela: Adrianna Sińska tel.: 4822 619 2512; 
email: adrianna.sinska@itr.lukasiewicz.gov.pl
Sprawy techniczne: Dariusz Kapelski tel.: 667 636 369;
email: dariusz.kapelski@itr.lukasiewicz.gov.pl 
Załącznik nr 1 do zapytania ofertowego nr 080/EZ/2024



